## Sheet1
StoneL Modbus VCT Data Table
Model Numbers: AMI95, QX95, QN95, EG95, EN95, Modbus I/O modules
I/O or Setting | I/O Register | Holding Register (Bit) | Values | Example
Closed Input | 10001 | 40002(8) | Logical (1 or 0) | To Read the Closed input: Read the Input Register 10001 or read the 9th bit of 16bit holding register 40002
Open Input | 10002 | 40002(9) | Logical (1 or 0) | To Read the Open input: Read the Input Register 10002 or read the 10th bit of 16bit holding register 40002
Output 1 | 1 | 40002(0) | Logical (1 or 0) | To Force Output1 : Write a 1 to output Register 00001 or to 1st bit of 16bit holding register 40002
Output 2 | 2 | 40002(1) | Logical (1 or 0) | To Force Output2 : Write a 1 to output Register 00002 or to 2nd bit of 16bit holding register 40002
Analog Input | 30001 | 40001 | 0- | To Read the Analog input: Read the 16bit holding register 40001
Watchdog Timer | 40003 |  | 0-100 (increments of 10) | To To Set Watchdog Timer to .5 seconds: Set register 40003 to 50
Slave Address | 40004 |  | 1-255(Default =3) | To change the Slave Address to 1: Set register 40004 to 1
Baud/Framing* | 40005 |  | 0-11 (Default =0)* | To set Baudrate and Framing to 38,400 baud, 8 data bits, no parity, 1 Stop bit): Set register 40005 to 8
* Register Value | Baud Rate | Framing
0 | 9600 | 8N1
1 | 9600 | 8E1
2 | 9600 | 8O1
3 | 9600 | 8N2
4 | 19200 | 8N1
5 | 19200 | 8E1
6 | 19200 | 8O1
7 | 19200 | 8N2
8 | 38400 | 8N1
9 | 38400 | 8E1
10 | 38400 | 8O1
11 | 38400 | 8N2